## Documentation
Title | WaTER - Model Input Output and Supplementary Calculations
Summary of File Contents | Summary of WaTER model inputs and outputs for three scenarios evaluated during S&T project 1877 - Cost Modeling of Membrane Desalination Processes Using Reclamation's WaTER Model. Used with the excel-based WaTER file 'S&T Project 1877 Model: WaTER - Model - 1877 Updates' The three scenarios evaluated include: Baseline (Case 1): Chemical Coagulation - Media Filtration - Electrodialysis Reversal (EDR), Case 2: Membrane Filtration - Nanofiltration, and Case 3: Electrocoagulation - Membrane Filtration - Nanofiltration. Spreadsheet tabs include: Flows and Recovery (Unit process flows and recovery for each scenario, including unit conversions), Water Quality (Foss Water Quality data used in modeling), Cost Summary (Summary of Capital and Operation and Maintenance (O&M), and Annual costs for each scenario), WaTER I_O (Inputs and Outputs to WaTER modules for each unit process for each scenario. Tab formatting reflects WaTER model formatting).
Author | Leah Flint
Publisher | Bureau of Reclamation
Date Published | 2026-05-06

## Flows and Recovery
Tab Description: | Summary of flows used for each unit process in WaTER model. Flows back calculated from treated water flows using unit process recovery
| Treated Water Flow | Value |  |  | Use during modeling
|  | MGD | m3/day | m3/yr
| Average Flow | 1.5 | 5681.8182 | 2073863.6364 | Operation and Maintenance Costs
| Maximum Flow | 2.3 | 8712.1212 | 3179924.2424 | System Sizing, Capital Costs
|  |  | Average Flow (MGD) |  | Maximum Flow (MGD)
| Process | Recovery | In | Out | In | Out
Basecase
| EDR | 68% | 2.2059 | 1.5 | 3.3824 | 2.3
| Media Filtration | 100% | 2.2059 | 2.2059 | 3.3824 | 3.3824
| Alum Coagulation | 100% | 2.2059 | 2.2059 | 3.3824 | 3.3824
| Overall | 68%
Case 2: MF-NF
| NF | 89% | 1.6854 | 1.5 | 2.5843 | 2.3
| MF | 90% | 1.8727 | 1.6854 | 2.8714 | 2.5843
| Overall | 80.1%
Case 3: EC - MF-NF
| NF | 89% | 1.6854 | 1.5 | 2.5843 | 2.3
| MF | 95% | 1.7741 | 1.6854 | 2.7203 | 2.5843
| EC | 100% | 1.7741 | 1.7741 | 2.7203 | 2.7203
| Overall | 84.55%

## Water Quality
Tab Description: | Water Quality inputs to WaTER model. Water quality sourced from DWPR report 192
November 2015 WQ, sourced from DWPR report 192
| Parameter | Value | Units
| Calcium | 287 | mg/L
| Magnesium | 218 | mg/L
| Sodium | 199 | mg/L
| Alkalinity (Bicarbonate) | 110 | mg/L as CaCO3
| Alkalinity (Carbonate) | 6 | mg/L as CaCO3
| Alkalinity (Total) [mg/L as CaCO3] | 116 | mg/L as CaCO3
| Chloride | 175 | mg/L
| Sulfate | 1624 | mg/L
| Silicon | 13.8 | mg/L
| Strontium | 8.8 | mg/L
| pH | 8 | s.u.
| TDS | 1950 | mg/L
| Conductivity | 2766 | uS/cm
| Turbidity | 2.2 | NTU
| DOC | 9.4 | mg/L
| UVA-254 | 0.11
| Temperature | 15C | C

## Baseline Cost Summary
Tab Description: | Case 1 / Baseline (Alum-MediaFiltration-EDR) Summary from WaTER model. Data summarized from Water I_O - Baseline tabs. Tables used directly in final report.
Process Flows
| Process | Recovery | Average Flow (MGD) |  | Maximum Flow (MGD) |  | Alternative Units [m3/yr]
|  |  | In | Out | In | Out | Out - Average | Out - Maximum
| Alum Coagulation | 100% | 2.2059 | 2.2059 | 3.3824 | 3.3824 | 3049799.4652 | 4676359.18
| Media Filtration | 100% | 2.2059 | 2.2059 | 3.3824 | 3.3824 | 3049799.4652 | 4676359.18
| EDR | 68% | 2.2059 | 1.5 | 3.3824 | 2.3 | 2073863.6364 | 3179924.2424
Captial Costs
| Cost | Process |  |  | Total
|  | Alum Coagulation | Media Filtration | EDR
| Capital Cost | 261154.7707 | 2827656.8686 | 11107800 | 14196611.6394
| Capital Recovery (Annual) | 18972.6098 | 0 | 806969.579 | 825942.1889
O&M Costs (no labor)
| O&M Category | Alum Coagulation | Media Filtration | EDR | Total
| Chemicals (Alum) | 131441.9345 | 0 | 0 | 131441.9345
| Media Replacement | 0 | 313959.24 | 0 | 313959.24
| Membrane Replacement | 0 | 0 | 457673.0098 | 457673.0098
| Maintenance/Materials | 378.4213 | 0 | 2580606.4198 | 2580984.841
| Labor | 0 | 0 | 583270 | 583270
O&M Costs (with labor)
| O&M Category | Alum Coagulation | Media Filtration | EDR | General WTP | Total
| Chemicals (Alum) | 131441.9345 | 0 | 0 | 0 | 131441.9345 |  | Cost outputs for the baseline option are summarized in Table 27. Energy use was calculated within the WaTER model for each unit process, and agreed within 2% with the actual energy use provided by FRMCD ($15,000 per month). The baseline option was calculated to have a capital cost of $14.2M, an annual operation cost of $5.3M, and a normalized cost of $2.55/m3 of water treated.
| Media Replacement | 0 | 313959.24 | 0 | 0 | 313959.24
| Membrane Replacement | 0 | 0 | 457673.0098 | 0 | 457673.0098
| Maintenance/Materials | 378.4213 | 0 | 2580606.4198 | 0 | 2580984.841
| Labor | 0 | 0 | 0 | 583270 | 583270
| Energy | 0 | 0 | 0 | 180000 | 180000
| Total O&M Costs | 131820.3557 | 313959.24 | 3038279.4296 | 763270 | 4247329.0253
O&M Costs (energy comparison to actuals)
|  | Process | Energy Cost
| WaTER Outputs (Annual) | Alum Coagulation | 475.562
|  | Media Filtration | 23706.3249
|  | EDR | 159606.499
|  | Total | 183788.3859
| Foss Information | Monthly Energy Cost | 15000
|  | Annual Energy Cost | 180000
| Percent Diference |  | 2.083%
Annual Costs
| Category | Alum Coagulation | Media Filtration | EDR | General WTP | Total
| Capital Recovery | 18972.6098 | 0 | 806969.579 |  | 825942.1889
| Operation and Mainteance Costs | 131820.3557 | 313959.24 | 3038279.4296 | 763270 | 4247329.0253
| Total Annual Costs | 150792.9655 | 313959.24 | 3845249.0087 | 763270 | 5073271.2142
| Normalized Annual costs ($/m3) | 0.072711 | 0.15139 | 1.8541 | 0.36804 | 2.4463

## Case 2 MF-NF Cost Summary
Tab Description: | Case 2 (MF-NF) Summary from WaTER model. Data summarized from Water I_O - Case 2 tabs. Tables used directly in final report.
Process Flows
| Process | Recovery | Average Flow (MGD) |  | Maximum Flow (MGD) |  | Alternative Units [m3/yr]
|  |  | In | Out | In | Out | Out - Average | Out - Maximum
| NF | 89% | 1.6854 | 1.5 | 2.5843 | 2.3 | 2073863.6364 | 3179924.2424
| MF | 90% | 1.8727 | 1.6854 | 2.8714 | 2.5843 | 2330183.8611 | 3572948.587
| Overall | 80.1%
Captial Costs
| Cost | MF | NF | Total
| Capital Cost | 1190370.8887 | 4781841.9791 | 5972212.8679
| Capital Recovery (Annual) | 86000 | 347395.6147 | 433395.6147
O&M Costs (no labor)
| O&M Category | MF | NF | Total
| Electricity | 11555.5591 | 48650.7185 | 60206.2776
| Membrane Replacement | 9000 | 119997.0447 | 128997.0447
| Cleaning Chemicals | 4000 | 6258.3863 | 10258.3863
| Cartridge Filters | 0 | 0 | 0
| Repairs and Replacement | 17000 | 44706.3536 | 61706.3536
| Insurance | 0 | 17882.5414 | 17882.5414
O&M Costs (with labor)
| O&M Category | MF | NF | General WTP | Total
| Electricity | 11555.5591 | 48650.7185 | 0 | 60206.2776
| Membrane Replacement | 9000 | 119997.0447 | 0 | 128997.0447
| Cleaning Chemicals | 4000 | 6258.3863 | 0 | 10258.3863
| Repairs and Replacement | 17000 | 44706.3536 | 0 | 61706.3536
| Insurance | 0 | 17882.5414 | 0 | 17882.5414
| Labor | 0 | 0 | 466616 | 466616 | Assume 4 staff days per day, one less than baseline and EC-MF-NF (one less unit process)
| Total O&M Costs | 41555.5591 | 237495.0445 | 466616 | 745666.6036
Annual Costs
| Category | MF | NF | General WTP | Total
| Capital Recovery | 86000 | 347395.6147 | 0 | 433395.6147
| Operation and Mainteance Costs | 41555.5591 | 237495.0445 | 466616 | 745666.6036
| Total Annual Costs | 127555.5591 | 584890.6592 | 466616 | 1179062.2183
| Normalized Annual costs ($/m3) | 0.061506 | 0.28203 | 0.225 | 0.56853

## Case 3 EC-MF-NF Cost Summary
Tab Description: | Case 3 (EC-MF-NF) Summary from WaTER model. Data summarized from Water I_O - Case 3 tabs. Tables used directly in final report.
Process Flows
| Process | Recovery | Average Flow (MGD) |  | Maximum Flow (MGD) |  | Alternative Units [m3/yr]
|  |  | In | Out | In | Out | Out - Average | Out - Maximum
| NF | 89% | 1.6854 | 1.5 | 2.5843 | 2.3 | 2073863.6364 | 3179924.2424
| MF | 95% | 1.7741 | 1.6854 | 2.7203 | 2.5843 | 2330183.8611 | 3572948.587
| EC | 100% | 1.7741 | 1.7741 | 2.7203 | 2.7203 | 2452825.1169 | 3760998.5126
| Overall | 84.55%
Captial Costs
| Cost | EC | MF | NF | Total
| Capital Cost | 3557228.267 | 1121970.8887 | 4686146.774 | 9365345.9297
| Capital Recovery (Annual) | 258000 | 82000 | 340443.4622 | 680443.4622
O&M Costs (no labor)
| O&M Category | EC | MF | NF | Total
| Electricity | 24034.0796 | 11555.5591 | 48650.7185 | 84240.3572
| Membrane Replacement |  | 4000 | 79998.0298 | 83998.0298
| Electrode Replacement | 159721.8501 |  |  | 159721.8501
| Cleaning Chemicals |  | 4000 | 4172.2575 | 8172.2575
| Cartridge Filters |  |  |  | 0
| Repairs and Replacement |  | 16000 | 44401.5343 | 60401.5343
| Insurance |  | 0 | 17760.6137 | 17760.6137
O&M Costs (with labor)
| O&M Category | EC | MF | NF | General WTP | Total
| Electricity | 24034.0796 | 11555.5591 | 48650.7185 |  | 84240.3572
| Membrane Replacement |  | 4000 | 79998.0298 |  | 83998.0298
| Electrode Replacement | 159721.8501 |  |  |  | 159721.8501
| Cleaning Chemicals |  | 4000 | 4172.2575 |  | 8172.2575
| Repairs and Replacement |  | 16000 | 44401.5343 |  | 60401.5343
| Insurance |  | 0 | 17760.6137 |  | 17760.6137
| Labor |  | 0 | 0 | 583270 | 583270 | Assume 5 staff days per day, same as baseline
| Total O&M Costs | 183755.9297 | 35555.5591 | 194983.1537 | 583270 | 997564.6425
Annual Costs
| Category | EC | MF | NF | General WTP | Total
| Capital Recovery | 258000 | 82000 | 340443.4622 | 0 | 680443.4622
| Operation and Mainteance Costs | 183755.9297 | 35555.5591 | 194983.1537 | 583270 | 997564.6425
| Total Annual Costs | 441755.9297 | 117555.5591 | 535426.616 | 583270 | 1678008.1048
| Normalized Annual costs ($/m3) | 0.21301 | 0.056684 | 0.25818 | 0.28125 | 0.80912

## WaTER I_O-Baseline-Alum
Tab Description: | Input, output and supplementary information for Case 1 Alum coagulation unit process evaluated using WaTER module Alum
Case 1 Baseline --> WaTER Alum module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 2.2059 | 2.2059
|  | Peak | 3.3824 | 3.3824
Supplementary Calculations and Information
|  | Target Concentration | ppm | 70 | 40-100, Dose changes with water temperature and turbidity
|  | Stock solution (Tote) strength | % | 50%
|  | Tote Volume (or weight) | lbs/gallon | 11.1 | Purchased in truck load 4000 gallons
|  | Cost per Tote | $/lb | 0.14
| WaTER Alum Module Input |  |  | Input to WaTER {k} Alum
WaTER Inputs
|  | Form | Liquid
|  | Cost per 100 lbs | 14 | $/lb (stock)
|  | Alternative dose | 70 | mg/L | Actual, not calculated from alkalinity
|  | Multiplier between liquid and solid | 2 |  | Accounts for 50% tote strength
| WaTER Alum Module Input |  |  | Output from WaTER {k} Alum
O&M Costs
|  | O&M Cost: |  | 2036.0659 | 1978 Costs
%
|  | Materials | 0.04 | 378.4213 | Today's Costs
|  | Energy | 0.59 | 475.562
|  | Labor | 0.37 | 680.4956
|  | Alum Cost: |  | 131441.9345
|  | January, 2023 Operation & Maintenance $: | 1 | 132976.4134
|  | Normalized Cost | Cost/treated volume
|  | January, 2023 O&M $/m3 plant effluent (with labor) | 0.06412
|  | January, 2023 O&M $/m3 plant effluent (with out labor) | 0.063792
Capital Costs
|  | Capital Cost: |  | 46573.3424 | 1978 Costs
|  | Use peak day flow/dose rate | %
|  | Manufactured & Electrical Equipment | 0.71 | 152827.6539 | Today's Costs
|  | Housing | 0.15 | 67581.9704
|  | Excavation, Site Work & Labor | 0.12 | 37280.6714
|  | Piping and Valves | 0.02 | 3464.475
|  | Steel | 0 | 0
|  | Concrete | 0 | 0
|  | January, 2023 Capital Cost $: | 1 | 261154.7707
|  | Amortized Capital Cost | 18972.6098
|  | Interest Rate | 6%
|  | Amortization Time | 30 | years

## WaTER I_O-Baseline-MediaF
Tab Description: | Input, output and supplementary information for Case 1 gravity media filtration unit process evaluated using WaTER module GravityFilt.
Case 1 Baseline --> WaTER GravityFilt module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 2.2059 | 2.2059
|  | Peak | 3.3824 | 3.3824
Supplementary Calculations and Information
FRMCD Data - Media Filtration
|  | type of media | Sand, Anthracite | --
|  | Area per filter | 684 | ft2
|  | number of filters | 2 | --
|  | full media replacement frequency | 50 | years | once since 1974, assume 50 yrs
|  | Partial media replacement frequency | yearly
|  | Partial media replacement approximate volume (or depth) | 3' to 4' yearly
|  | Backwash frequency per filter cell | 1 | backwash per week
|  | backwash duration | 20 | min | Total cell downtime
| WaTER GravityFilt Module Input |  |  | Input to WaTER {w} GravityFilt
WaTER Inputs
Inputs to WaTER
|  | Wash Cycle | 168 | hours
|  | Media Depth | 3.5 | ft | Average of yearly replacement
|  | Alternative Bed Area: | 127.1375 | m2
|  | Backwash duration | 20
| WaTER GravityFilt Module Output |  | Output from WaTER {w} GravityFilt
O&M Costs
|  | 1978 O&M Cost: | % | 30915.9167
|  | Materials |  | 0
|  | Energy | 0.36 | 23706.3249
|  | Labor | 0.52 | 62173.0159
|  | Filter media replacement |  | 313959.24
|  | January, 2023 Operation & Maintenance $: |  | 399838.5808
|  | Normalized Cost | Cost/treated volume
|  | January, 2023 O&M $/m3 plant effluent | 0.1928
|  | January, 2023 O&M $/m3 plant effluent (with out labor) | 0.16282
Capital Costs
|  | 1978 Capital Cost: | % | 634319.994
|  | Manufactured & Electrical Equipment | 0.26 | 762233.338
|  | Housing | 0.18 | 336603.44
|  | Excavation, Site Work & Labor | 0.22 | 641508.9368
|  | Piping and Valves | 0.23 | 677891.1346
|  | Steel | 0.05 | 97164.2737
|  | Concrete | 0.06 | 312255.7455
|  | January, 2023 Capital Cost $: | 1 | 2827656.8686

## WaTER I_O - Baseline-EDR
Tab Description: | Input, output and supplementary information for Case 1 EDR unit process evaluated using WaTER module ED2. Yellow cells are user-defined inputs
Case 1 Baseline --> WaTER ED2 module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 2.2059 | 1.5
|  | Peak | 3.3824 | 2.3
Supplementary Calculations and Information
|  | Parameter | Units | Value
|  | percent recovery | % | 68
|  | Number of sets of EDR modules | # | 3
|  | number of stages (in series) | # | 3
|  | # EDR lines per set | # | 8
|  | Voltage to each unit | V | 320-360
|  | Amperage draw per unit | A | 12-13
|  | # anionic membranes per cell | # | 600
|  | # cationic membranes per cell | # | 599
|  | # feed spacers per cell | # | 1200
|  | # heavy cation membranes per cell | # | 2
|  | # heavy anion membranes per cell | # | 2
|  | # electrode spacers per cell | # | 2
|  | # (-) electrode per cell | # | 1
|  | # (+) electrode per cell | # | 1 | $/area
|  | Cost per membrane (anionic or cationic) | $/membrane | 51
|  | cost per feed spacer | $/spacer | 26
|  | cost per heavy cation membrane | $/membrane | 125
|  | cost per electrode feed spacer | $/spacer | 95
|  | Cost per electrode (+ or -) | $/electrode | 3000
|  | Polarity reversal frequency | min | 17
|  | Membrane life (approx) | years | 15
|  | Membrane life for modeling | years | 10
|  | Membrane replacement cost (accounting for all) |  | 186.5476
Membrane Area
Assume 2 trains for avg flow, 3 trains for max flow
|  | Number Stacks per train | 24
|  | Membrane pairs per stack | 600
|  | Membrane area per membrane pair | 0.85 | m2
|  | membrane area per stack | 510 | m2
|  | membrane area per train | 12240
|  | Membranes pairs per train | 14400
|  | Number trains average flow | 2
|  | Membrane surface area, Average Flow | 24480
|  | Membrane pairs, Average Flow | 28800
| WaTER ED2 Module Input |  | See Screenshot | Input to WaTER {ee} ED2 tabs
WaTER Inputs
|  | Percent Recovery | 68% | %
|  | Area/membrane pair | 0.85 | m2 | total single membrane area: 18.25” x 40.25” Active membrane area is 0.85m2 (https://www.watertechnologies.com/products/ionics-ion-exchange-membranes)
|  | Diluate side resistance | 0.00134 | (ohms/cm)/cm2 | Based on WQ
|  | Concentrate side resistance | 0.00022222 | (ohms/cm)/cm2 | Based on WQ
|  | Membrane resistance | 2.5 | (ohms/cm)/cm2: | Suggested value in DWPR report 93
|  | Current Desnsity | 14.7059 | amps/m2 | Amp draw per unit is 12-13 A
|  | Current Efficiency | 95% | % | Suggested value in DWPR report 93
|  | Membrane voltage potential | 0.56667 | V/Membrane pair | 340 V, 600 membrane pairs per cell
|  | Pumping requirements | 0 | kWhr/m3 | FRMCD WTP does not recirculate within EDR, other pumping costs excluded
|  | Membrane cost | 186.5476 | $/m2
|  | Membrane life expectancy | 10 | years
|  | Concstruction Cost Factor | 165%
|  | Membrane surface area, Average Flow | 24480 |  | 600 membrane pairs per stack, 24 stacks per train, 2 trains at average flow
|  | Shifts per day | 1 | #/day | All labor included for EDR
|  | Workers per shift | 5 | #/shift
| WaTER ED2 Module Output |  | Output from WaTER {ee} ED2 tabs
O&M Costs
First Stage O&M Costs/ year
|  | Chemicals | 0
|  | Maintenance | 2580606.4198
|  | Membrane Replacement: | 457673.0098
|  | Labor Cost: | 583270
|  | ED Electicity Cost/year @ $0.0639/kWhr: | 159606.499
|  | Capital Recovery | 806969.579
|  | January, 2023 O&M $: | 4154767.5217
|  | January, 2023 O&M $/m3 treated: | 2.0049
First Stage O&M Costs/ year (w/out labor)
|  | Chemicals | 0
|  | Maintenance | 2580606.4198
|  | Membrane Replacement: | 457673.0098
|  | Labor Cost: | 0
|  | ED Electicity Cost/year @ $/kWhr: | 159606.499
|  | Capital Recovery | 806969.579
|  | January, 2023 O&M $: | 3571497.5217
|  | January, 2023 O&M $/m3 treated: | 1.7235
Capital Costs
|  | Based on Membrane Cost @ $187/m2 | 11107800

## WaTER I_O - Case 2 MF
Tab Description: | Input, output and supplementary information for Case 2 MF unit process evaluated using WaTER module MF-P tabs. Yellow cells are user-defined inputs
Case 2 MF-NF --> WaTER MF-P module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 1.8727 | 1.6854
|  | Peak | 2.8714 | 2.5843
Supplementary Calculations
|  | Parameter | Value | Units | Source
|  | Flow Rate | 1833093.1 | gpd | WAVE (gross filtrate)
|  | Number modules (trains) | 2 |  | WAVE
|  | Membranes per module | 42 |  | WAVE
|  | Total number membranes | 84 |  | WAVE
|  | Flow per membrane | 21822.5369 | gpd | Calculated
|  | Flow per membrane | 15.1545 | gpm | Calculated
|  | Flow per module | 636.4907 | gpm | Calculated
|  | Backwash flux | 100 | LMH | WAVE
|  | Membrane area (per membrane) | 77 | m2 | WAVE, specific to SFD-2880
|  | Membrane area (per module) | 3234 | m2
|  | backwash flow rate per module | 1166.9824 | gpm
| WaTER MF-P Module Input |  | See Screenshot | Input to WaTER {z} MF-P Input and {aa} MF-P Output tabs
WaTER Inputs
|  | Parameter | Value | Units | Notes
|  | Membrane Module equipment cost | 211500 |  | WaTER recommended cost
|  | Cost per membrane | 1100 |  | SFD-2880 watersurplus.com
|  | modular system flow rate | 636.4907 | gpm | Calculated from WAVE output
|  | Flow per module | 15.1545 | gpm | Calculated from WAVE output
|  | No. membranes per module | 42 |  | WAVE output
|  | Pump efficiency | 80 | % | WaTER recommended value
|  | Motor efficiency | 93 | % | Water recommended value
|  | Design feed pressure | 30 | psi | WAVE output
|  | Backflush pressure | 30 | psi | WAVE output
|  | Backwash Flow | 1166.9824 | gpm | Calculated from Texas A&M design, WAVE output
|  | Backwash intervals | 60 | minutes | Texas A&M design
|  | Backwash and backflush duration | 4.3 | minutes | WAVE output, targeting Texas A&M design
|  | Sodium Hypochlorite Cost | 0.37692 | $/L | WAVE-suggested cost
|  | Design dosage | 300 | mg/L | Texas A&M experiments, as NaOCl
|  | Specific gravity (NaOCl) | 1.168
|  | Solution concentration | 12 | % | Typical value
|  | Membrane Life | 10 | Years | Typical value
|  | Staff Days/day | 0 |  | Labor applied to full treatment process, not unit processes
|  | Building | 100 | $/ft2 | WaTER recommnded value, indexed for year
|  | Installation | 70000 | $/90M10C | WaTER recommnded value, indexed for year
|  | Miscellaneous | 5 | % of Module Cost | WaTER recommnded value
|  | Plant interconnecting piping | 10 | % of Module and misc. | WaTER recommnded value
|  | Engineering | 10 | % of Module and misc. | WaTER recommnded value
| WaTER MF-P Module Output |  |  | Output from WaTER {z} MF-P Input and {aa} MF-P Output tabs
O&M Costs
|  | Electricity | 11555.5591
|  | Labor | 0
|  | Chemicals (Sodium Hypochlorite) | 3000
|  | Membrane Replacement | 9000
|  | Cleaning Chemicals(NaOCl) | 1000
|  | Repairs and Replacement and Misc. | 17000
|  | Total O & M Cost | 41555.5591
Capital Costs
Indirect Capital Costs
|  | Interest During Construction | 6 | % of Total direct
|  | Contingencies | 20 | % of Total direct
|  | A&E Fees, Proj. Management | 10 | % of Total direct
|  | Working Capital | 20 | % of Total direct
|  | Total Direct Capital Costs | 850370.8887
Indirect Capital Costs
|  | Interest During Construction | 51000 |  | 6 | % of Total direct
|  | Contingencies | 170000 |  | 20 | % of Total direct
|  | A&E Fees, Proj. Management | 85000 |  | 10 | % of Total direct
|  | Working Capital | 34000 |  | 4 | % of Total direct
|  | Total Indirect Captial Cost | 340000
Total Costs
|  | Total Construction Cost | 1190370.8887
|  | Cost per gpd capacity | 0.70029
Total costs
|  | Capital Recovery | 86000
|  | O&M | 41555.5591
|  | Annual cost | 127555.5591
|  | $/m3 Product | 0.054276
|  | $/1000 gal Product | 0.20559
|  | $/acre foot Product | 66.9441

## WaTER I_O - Case 2 NF
Tab Description: | Input, output and supplementary information for Case 2 NF unit process evaluated using WaTER module RO&NF tabs. Yellow cells are user-defined inputs
Case 2 MF-NF --> WaTER RO/NF module
| Process Flows |  |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 1.6854 | 1.5
|  | Peak | 2.5843 | 2.3
| WaTER RO&NF Module Input |  | See Screenshot | Input to WaTER {f} RO&NF Input and {g} RO&NF Output tabs
Membrane Manufacturer Specifications
|  | Membrane Manufacturer | DOW FilmTec
|  | Model # | NF270-400
|  | Membrane Diameter | 20.32 | (10.16 or 20.32 cm)
|  | Productivity | 47 | m3/day
|  | Area per module | 37.1 | m2
|  | Operating pressure, Papp | 482 | kPa
|  | Test solution TDS | 2000 | mg/L
|  | Avg. MW of TDS, | 120 | mg/mmole NaCl
|  | Chloride Rejection | 50 | %
|  | Sulfate Rejection | 97 | %
|  | Recovery Rate | 15 | %
|  | Temperature | 25 | oC
RO&NF Input Module Inputs
|  | Parameter | Input Value | Units | Notes
|  | Net driving pressure , NDPi | 482.5 | kPa | Target 70 psi
|  | Number of elements per vessel | 6 | elements / vessel
|  | Number of Skids (manual input) | 2 | skids
|  | Recovery Rate | 0.89 | Decimal | Input on {e} Report
|  | Administrative Area | 0 | m2 | Neglect Building
|  | Odor Control? | N | Yes (Y) or No (N) | Neglect Odor Control
|  | Emergency Generatore Size | 0 | MW | Neglect Generator
|  | High Pressure Feed Pump | Y | Yes (Y) or No (N)
|  | Pump Style | CSS | *PD, VST or CSS
|  | Height DIfference | 3 | m | Typical values in WaTER
|  | Motor Efficiency | 0.75 |  | Typical values in WaTER
|  | Pump Efficiency | 0.75 |  | Typical values in WaTER
|  | Coupling Efficiency | 1 |  | Typical values in WaTER
|  | Number of Pumps | 2 |  | Typical values in WaTER
|  | Energy Recovery for Seawater | N | Yes (Y) or No (N) | Neglect - Brackish Water not Seawater
|  | Transfer Pumps (to HPP) | N | Yes (Y) or No (N) | Neglect transfer pumps
|  | Product Water Pump | N | Yes (Y) or No (N) | Neglect product water pump
|  | Cleaning Rate | 6 | per Year
|  | Staff Days/day | 0 |  | Adjusted after for full WTP
|  | Flux Target | 35 | LMH | Adjust Factor (cell J7) after rest of module set up
|  | Factor | 0.83
RO&NF Output Module Inputs
|  | Parameter | Input Value | Units | Notes
|  | Membranes | 1047 | $/module | Actual cost (2023-2024 data)
|  | RO Skids | 3000 | $/Vessel | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Electrical | 977 | $/m3 | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Insturmentation & Controls | 65000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Process Piping | 55000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Yard Piping | 50000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Cartridge Filters | 0 |  | Neglected across analysis (EDR and NF)
|  | Membrane Cleaning Equip | 67000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Contractor Engineering & Training | 100000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Concentrate Treatment & Piping | 13.21 | $/m3 | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Sitework | 14.53 | $/m3 | Neglected because not included in other estimates
| RO&NF Module Outputs |  | Output from WaTER {f} RO&NF Input and {g} RO&NF Output tabs
O&M Costs
Estimating O&M Costs
|  | Electricity | 48650.7185
|  | Labor | 0
|  | Membrane Replacement | 119997.0447
|  | Cleaning Chemicals | 6258.3863
|  | Cartridge Filters | 0
|  | Repairs and Replacement | 44706.3536
|  | Insurance | 17882.5414
|  | Lab fees | 0
|  | Total O&M Cost | 237495.0445
Captial Costs
|  | Total Direct Capital Costs | 3370226.7621
Indirect Capital Costs
|  | Interest During Construction | 204936.0848
|  | Contingencies | 683120.2827
|  | A&E Fees, Proj. Management | 341560.1414
|  | Working Capital | 136624.0565
|  | Total Indirect Captial Cost | 1366240.5655
|  | Total Construction Cost | 4781841.9791
Total Costs
|  | Cost per m3/day capacity | 749.5974
|  | Cost per gpd capacity | 2.8372
Total Costs
|  | Capital Recovery | 347395.6147
|  | O&M | 217295.1309
|  | Annual cost | 564690.7456
|  | $/m3 Product | 0.24252
|  | $/1000 gal Product | 0.91794
|  | $/acre foot Product | 299.1263

## WaTER I_O - Case 3 EC
Tab Description: | Input, output and supplementary information for Case 3 EC unit process evaluated using WaTER module Electrocoagulation tab. Yellow cells are user-defined inputs
Case 3 EC-MF-NF --> WaTER EC module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 1.7741 | 1.7741
|  | Peak | 2.7203 | 2.7203
| WaTER EC Module Input and Output |  | See Screenshot | Input to WaTER {nn} Electrocoagulation tabs
|  | Current Density | 10
|  | Voltage (cell potential) | 2.2
|  | Blade Area | 16.5
|  | Treatment Time | 600
|  | Treatment volume | 0.4
|  | Anode Material | Aluminum
|  | Faradic Efficiency (%) | 115%
|  | Electrode Use Percentage | 75%
|  | Power Efficiency | 0.9
|  | Electrode material cost | 1.8
|  | Electrode blade purity | 99%
|  | Operator full time equivalents | 1.5
|  | Operation Costs |  | Units | Alternative Units |  | Notes
|  | Unit Electricity Cost | 0.0639 | $/kWh
|  | Power Efficiency | 0.9 |  |  |  | Typical value, converting from AC to DC
|  | Specific Energy Cost | 0.0096649 | $/m3 | 0.036582 | $/1000 gallon
|  | Annual Energy Cost | 24034.0796 | $/year
|  | Electrode material cost | 1.8 | $/kg | 0.81648 | $/lb | Aluminum is $1.8/kg from Alavijeh et al., 2022
|  | Electrode blade purity | 99%
|  | Specific Electrode Cost | 0.064229 | $/m3 | 0.24311 | $/1000 gallon
|  | Annual Electrode Cost | 159721.8501 | $/year
|  | Hourly Operator Cost | 39.95 | $/hr
|  | Operator full time equivalents | 0 |  |  |  | Labor included in General WTP
|  | Specific Labor Cost | 0 | $/m3 | 0 | $/1000 gallon
|  | Annual Labor Cost | 0 | $/year
|  | Sum Specific Operating Costs | 0.074 | $/m3 | 0.28 | $/1000 gallon
|  | Sum Annual Operating Costs | 183755.93 | $/year
Capital Costs
|  | Plant Cost (Reference Year) | 1004916.0625
|  | Construction Cost Index (Reference Year) | 5210 |  |  |  | 1993
|  | Construction Cost Index (Analysis Year) | 13175.03
|  | Adjusted Capital Cost | 2541228.267
Indirect Capital Costs
|  | Interest During Construction | 152000 |  | 6 | % of Total direct
|  | Contingencies | 508000 |  | 20 | % of Total direct
|  | A&E Fees, Proj. Management | 254000 |  | 10 | % of Total direct
|  | Working Capital | 102000 |  | 4 | % of Total direct
|  | Total Indirect Captial Cost | 1016000
|  | Total Capital Costs | 3557228.267
Total Costs
Total costs
|  | Amortization time | 30 |  |  |  | Plant Life = 30 years
|  | Interest Rate | 6%
|  | Capital Recovery | 258000
|  | O&M | 183755.9297
|  | Annual cost | 441755.9297
|  | $/m3 Product | 0.17764 | 0.67239 | $/1000 gal Product

## WaTER I_O - Case 3 MF
Tab Description: | Input, output and supplementary information for Case 3 MF unit process evaluated using WaTER module MF-P tabs. Yellow cells are user-defined inputs
Case 3 EC-MF-NF --> WaTER RO/NF module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 1.7741 | 1.6854
|  | Peak | 2.7203 | 2.5843
Supplementary Calculations
|  | Parameter | Value | Units | Source
|  | Flow Rate | 1756541 | gpd | WAVE (gross filtrate)
|  | Number modules (trains) | 2 |  | WAVE
|  | Membranes per module | 20 |  | WAVE
|  | Total number membranes | 40 |  | WAVE
|  | Flow per membrane | 43913.525 | gpd | Calculated
|  | Flow per membrane | 30.4955 | gpm | Calculated
|  | Flow per module | 609.9101 | gpm | Calculated
|  | Backwash flux | 100 | LMH | WAVE
|  | Membrane area (per membrane) | 77 | m2 | WAVE, specific to SFD-2880
|  | Membrane area (per module) | 1540 | m2
|  | backwash flow rate per module | 555.7059 | gpm
| WaTER MF-P Module Input |  | See Screenshot | Input to WaTER {z} MF-P Input and {aa} MF-P Output tabs
WaTER Inputs
|  | Parameter | Value | Units | Notes
|  | Membrane Module equipment cost | 211500 |  | WaTER recommended cost
|  | Cost per membrane | 1100 |  | SFD-2880 watersurplus.com
|  | modular system flow rate | 609.9101 | gpm | Calculated from WAVE output
|  | Flow per module | 30.4955 | gpm | Calculated from WAVE output
|  | No. membranes per module | 20 |  | WAVE output
|  | Pump efficiency | 80 | % | WaTER recommended value
|  | Motor efficiency | 93 | % | Water recommended value
|  | Design feed pressure | 30 | psi | WAVE output
|  | Backflush pressure | 30 | psi | WAVE output
|  | Backwash Flow | 556 | gpm | Calculated from Texas A&M design, WAVE output
|  | Backwash intervals | 60 | minutes | Texas A&M design
|  | Backwash and backflush duration | 4.3 | minutes | WAVE output, targeting Texas A&M design
|  | Sodium Hypochlorite Cost | 0.37692 | $/L | WAVE-suggested cost
|  | Design dosage | 300 | mg/L | Texas A&M experiments, as NaOCl
|  | Specific gravity (NaOCl) | 1.168
|  | Solution concentration | 12 | % | Typical value
|  | Membrane Life | 10 | Years | Typical value
|  | Staff Days/day | 0 |  | Labor applied to full treatment process, not unit processes
|  | Building | 100 | $/ft2 | WaTER recommnded value, indexed for year
|  | Installation | 70000 | $/90M10C | WaTER recommnded value, indexed for year
|  | Miscellaneous | 5 | % of Module Cost | WaTER recommnded value
|  | Plant interconnecting piping | 10 | % of Module and misc. | WaTER recommnded value
|  | Engineering | 10 | % of Module and misc. | WaTER recommnded value
Indirect Capital Costs
|  | Interest During Construction | 6 | % of Total direct
|  | Contingencies | 20 | % of Total direct
|  | A&E Fees, Proj. Management | 10 | % of Total direct
|  | Working Capital | 4 | % of Total direct
| WaTER MF-P Module Output |  |  | Output from WaTER {z} MF-P Input and {aa} MF-P Output tabs
O&M Costs
|  | Electricity | 11555.5591
|  | Labor | 0
|  | Chemicals (Sodium Hypochlorite) | 3000
|  | Membrane Replacement | 4000
|  | Cleaning Chemicals(NaOCl) | 1000
|  | Repairs and Replacement and Misc. | 16000
|  | Total O & M Cost | 35555.5591
Capital Costs
|  | Total Direct Capital Costs | 801970.8887
Indirect Capital Costs
|  | Interest During Construction | 48000 |  | 6 | % of Total direct
|  | Contingencies | 160000 |  | 20 | % of Total direct
|  | A&E Fees, Proj. Management | 80000 |  | 10 | % of Total direct
|  | Working Capital | 32000 |  | 4 | % of Total direct
|  | Total Indirect Captial Cost | 320000
Total Costs
|  | Total Construction Cost | 1121970.8887
|  | Cost per gpd capacity | 0.66005
Total costs
|  | Capital Recovery | 82000
|  | O&M | 35555.5591
|  | Annual cost | 117555.5591
|  | $/m3 Product | 0.050021
|  | $/1000 gal Product | 0.18947
|  | $/acre foot Product | 61.6959

## WaTER I_O - Case 3 NF
Tab Description: | Input, output and supplementary information for Case 3 NF unit process evaluated using WaTER module RO&NF tabs.
Case 3 EC-MF-NF --> WaTER RO/NF module
| Process Flows |  | Input to WaTER {b} Capacity
Process Flows (MGD)
|  |  | Influent | Effluent
|  | Average | 1.6854 | 1.5
|  | Peak | 2.5843 | 2.3
| WaTER RO&NF Module Input |  | See Screenshot | Input to WaTER {f} RO&NF Input and {g} RO&NF Output tabs
Membrane Manufacturer Specifications
|  | Membrane Manufacturer | DOW FilmTec
|  | Model # | NF270-400
|  | Membrane Diameter | 20.32 | (10.16 or 20.32 cm)
|  | Productivity | 47 | m3/day
|  | Area per module | 37.1 | m2
|  | Operating pressure, Papp | 482 | kPa
|  | Test solution TDS | 2000 | mg/L
|  | Avg. MW of TDS, | 120 | mg/mmole NaCl
|  | Chloride Rejection | 50 | %
|  | Sulfate Rejection | 97 | %
|  | Recovery Rate | 15 | %
|  | Temperature | 25 | oC
RO&NF Input Module Inputs
|  | Parameter | Input Value | Units | Notes
|  | Net driving pressure , NDPi | 482.5 | kPa | Target 70 psi
|  | Number of elements per vessel | 6 | elements / vessel
|  | Number of Skids (manual input) | 2 | skids
|  | Recovery Rate | 0.89 | Decimal | Input on {e} Report
|  | Administrative Area | 0 | m2 | Neglect Building
|  | Odor Control? | N | Yes (Y) or No (N) | Neglect Odor Control
|  | Emergency Generatore Size | 0 | MW | Neglect Generator
|  | High Pressure Feed Pump | Y | Yes (Y) or No (N)
|  | Pump Style | CSS | *PD, VST or CSS
|  | Height DIfference | 3 | m | Typical values in WaTER
|  | Motor Efficiency | 0.75 |  | Typical values in WaTER
|  | Pump Efficiency | 0.75 |  | Typical values in WaTER
|  | Coupling Efficiency | 1 |  | Typical values in WaTER
|  | Number of Pumps | 2 |  | Typical values in WaTER
|  | Energy Recovery for Seawater | N | Yes (Y) or No (N) | Neglect - Brackish Water not Seawater
|  | Transfer Pumps (to HPP) | N | Yes (Y) or No (N) | Neglect transfer pumps
|  | Product Water Pump | N | Yes (Y) or No (N) | Neglect product water pump
|  | Cleaning Rate | 6 | per Year
|  | Staff Days/day | 0 |  | Adjusted after for full WTP
|  | Flux Target | 41 | LMH | Adjust Factor (cell J7) after rest of module set up
|  | Factor | 0.98
RO&NF Output Module Inputs
|  | Parameter | Input Value | Units | Notes
|  | Membranes | 1047 | $/module | Actual cost (2023-2024 data)
|  | RO Skids | 3000 | $/Vessel | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Electrical | 977 | $/m3 | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Insturmentation & Controls | 65000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Process Piping | 55000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Yard Piping | 50000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Cartridge Filters | 0 |  | Neglected across analysis (EDR and NF)
|  | Membrane Cleaning Equip | 67000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Contractor Engineering & Training | 100000 |  | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Concentrate Treatment & Piping | 13.21 | $/m3 | Base cost, suggested value in WaTER Module, adjusted with ENR indices
|  | Sitework | 14.53 | $/m3 | Neglected because not included in other estimates
| RO&NF Module Outputs |  | Output from WaTER {f} RO&NF Input and {g} RO&NF Output tabs
O&M Costs
Estimating O&M Costs
|  | Electricity | 48650.7185
|  | Labor | 0
|  | Membrane Replacement | 79998.0298
|  | Cleaning Chemicals | 4172.2575
|  | Cartridge Filters | 0
|  | Repairs and Replacement | 44401.5343
|  | Insurance | 17760.6137
|  | Lab fees | 0
|  | Total O&M Cost | 194983.1537
Capital Costs
|  | Total Direct Capital Costs | 3347247.6957
Indirect Capital Costs
|  | Interest During Construction | 200834.8617
|  | Contingencies | 669449.5391
|  | A&E Fees, Proj. Management | 334724.7696
|  | Working Capital | 133889.9078
|  | Total Indirect Captial Cost | 1338899.0783
Total Costs
|  | Total Construction Cost | 4686146.774
|  | Cost per m3/day capacity | 734.5963
|  | Cost per gpd capacity | 2.7804
Total Costs
|  | Capital Recovery | 340443.4622
|  | O&M | 194983.1537
|  | Annual cost | 535426.616
|  | $/m3 Product | 0.22995
|  | $/1000 gal Product | 0.87037
|  | $/acre foot Product | 283.6246

## WAVE IO
Tab Description: | Input, output and supplementary information for DuPONT WAVE modeling. WAVE is a DuPont membrane estimate software and was used to configure MF and NF full-scale systems for subsequent analysis by WaTER. WAVE Input/output files included as appendix is final report.
MF
WAVE Supplementary MF Calculations
Sodium Hypochlorite Cost adjustment to WaTER input units
|  | Unit | Value
|  | WAVE $/day | 1.47
|  | WAVE L/day | 3.9
|  | $/L (WaTER input) | 0.37692
WAVE MF Inputs and Outputs
|  |  | Case 2 - Without EC | Case 3 - With EC
|  | Membrane | Dupont SFD-2880 | Dupont SFD-2880
|  | Membrane area per module (m2) | 77 | 77
|  | MF Product flow rate (MGD) | 1.68 | 1.68
|  | Total UF Trains | 2 | 2
|  | UF modules per train | 42 | 20
|  | Total UF modules | 84 | 40
|  | Filtration Interval (minutes) | 60 | 60
|  | Backwash duration (minutes) | 4.3 | 4.3
|  | Backwash flux (LMH) | 100 | 100
|  | Recovery (calculated by WAVE) | 92% | 96%
|  | Filtration flux (calculated by WAVE) (LMH) | 49 | 97
NF
WAVE Supplementary NF Calculations
|  | Case | Case 2 - Without EC | Case 3 - With EC
|  | Initial Flux from Sari and Chellam, 2017 [LMH] | 43 | 43
|  | Flux decline reported by Sari and Chellam, 2017 | 36% | 8%
|  | Average flux (target for WAVE modeling) [LMH] | 35 | 41
WAVE NF Inputs and Outputs
|  | Parameter | Case 2 - Without EC | Case 3 - With EC
|  | Membrane | DOW Filmtec NF 270 | DOW Filmtec NF 270
|  | Total Number Elements | 180 | 162
|  | Stage 1 number pressure vessels | 20 | 18
|  | Stage 2 number pressure vessels | 10 | 9
|  | Elements per pressure vessel | 6 | 6
|  | Average Flux | 35.4 | 39.3
|  | Recovery | 89% | 89%
Overall
WAVE Energy and Costs
|  | Parameter | Case 2 - Without EC | Case 3 - With EC
|  | MF Specific Energy (kWh/m3) | 0.07 | 0.08
|  | MF Operating Costs - Energy Only ($/m3) | 0.005 | 0.005
|  | NF Specific Energy (kWh/m3) | 0.34 | 0.37
|  | NF Operating Costs - Energy Only ($/m3) | 0.021 | 0.023