## Metadata
Metadata
Dataset Title | Insulation Resistance and Polarization Index Testing of Generator Stator and Field Windings
Authors | Eric Eastment
Publisher | Bureau of Reclamation
Publisher Location | Denver, CO, USA
Dataset Publication Date | 2026-03-13
Link to RISE Catalog Item | https://data.usbr.gov/catalog/8534/item/133949
Associated S&T Project | S&T Project 20100: Evaluation of Alternative Fire Suppression Methods for Generators for Improved Safety, Effectiveness and Reliability
Dataset Description | This dataset contains baseline and post‑fault Insulation Resistance (IR) and Polarization Index (PI) test results for generator stator windings and field windings. Testing was performed using a Megger S1‑1568 insulation tester. The dataset includes: Baseline testing for Phase A, Phase B, Phase C, Bulk (3‑phase), and Field Winding After‑Fault #1 (CO₂ suppression) – tests not performed because suppression media did not enter the air housing After‑Fault #2 (Hybrid Water Mist media) – IR/PI test results included After‑Fault #3 (Hybrid Water Mist media) – IR/PI test results included Measurements include corrected IR readings (to 40°C), PI values, leakage current (µA), environmental conditions (temperature, humidity), and test voltages (500–5103 Vdc).
Purpose of Data Collection | To evaluate generator stator and field winding insulation health under baseline conditions and after exposure to various fire suppression media, providing quantitative IR and PI metrics used to assess degradation or confirm compliance with minimum acceptable thresholds.
Data Collection Methods | IR and PI tests were performed using a Megger S1‑1568 insulation tester. PI = IR at 10 minutes / IR at 1 minute. IR values were corrected to 40°C using the instrument’s standard correction factor. Tests followed standard generator insulation test procedures for baseline, bulk, and field windings. Environmental conditions (ambient temperature, RTD temperature, humidity) were recorded during each test sequence.
QA/QC Procedures | Test Instrument calibration verified via Megger S1‑1568 Temperature corrections applied uniformly to IR values per IEEE 43 standard for thermoplastic insulation systems. Minimum acceptance criteria noted in test records: Min Allowed PI = 1.0 (Not based on IEEE standard. Exception is based on subject matter expert experience and extreme conditions imposed on the generator during repeat fault testing and short-duration operation of the generator (experiment performed prior to refurbishment). Min Allowed IR1 = 18 MΩ (phase tests) Min Allowed IR1 = 7.1 MΩ (3‑phase bulk configuration) Min Allowed IR1 = 80 kΩ (field winding) Fault #1 test excluded due to lack of media exposure; documented accordingly in report.
Data Processing Information | Raw test tables were reorganized into structured tabular format. Data was entered manually into spreadsheet as readings appeared on the test instrument. Time steps (15s – 600s) and measurements are preserved as captured. Notes from operators were transferred into the “Notes” field.
Geographic/Location Information | Testing performed on Hydroelectric Generator. Location type: Hydroelectric Powerplant - Asset = Generator.
Units and Measurement Definitions | IR: GΩ (corrected to 40°C) Leakage Current: µA Test Voltage: Vdc PI: dimensionless ratio (IR₆₀₀s / IR₆₀s) Temperature: °C Humidity: % Relative Humidity
Acronyms and Definitions | IR – Insulation Resistance PI – Polarization Index RTD – Resistance Temperature Detector HWM – Hybrid Water Mist CO₂ – Carbon Dioxide suppression system GΩ / MΩ – Gigaohm / Megaohm µA – Microampere
Limitations & Notes | Fault #1 IR/PI tests were not performed because suppression media did not enter the air housing. Baseline Field Winding test file did not save complete data, noted in source Excel. PI and IR minimum acceptable values should be interpreted according to generator manufacturer or Reclamation maintenance guidelines. Some environmental readings vary slightly due to test operator timing.
Recommended Citation | Bureau of Reclamation. 2026. Insulation Resistance and Polarization Index Testing of Generator Stator and Field Windings. Bureau of Reclamation, Technical Service Center, Denver, Colorado.

## Generator Baseline IR&PI Data
Baseline (pre-fault testing) Data - Generator Stator and Field Winding Insulation Resistance (IR) and Polarization Index (PI) Test Results
Phase A |  |  |  | Phase B |  |  |  | Phase C |  |  |  | Bulk Test (Phase A, B, & C connected together - tested simultaneously) |  |  |  | Field Winding
Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568
Date | 2024-11-25 | Start Time | 0800 | Date | 2024-11-25 | Start Time | 0812 | Date | 2024-11-25 | Start Time | 0812 | Date | 2024-11-25 | Start Time | 0846 | Date | 2024-11-15 | Start Time | 0735
Ambient Temp | 18.7 |  | C | Ambient Temp | 18.7 |  | C | Ambient Temp | 18.7 |  | C | Ambient Temp | 18.7 |  | C | Ambient Temp | 18.6 |  | C
RTD Temp | 20 | by IR | C | RTD Temp | 20.1 |  | C | RTD Temp | 20.1 |  | C | RTD Temp | 20.1 |  | C | Winding IR Temp | 21.8 | by IR | C
Humidity | 29.3 |  | % R/H | Humidity | 26.8 |  | % R/H | Humidity | 26.8 |  | % R/H | Humidity | 26.8 |  | % R/H | Humidity | 34.6 |  | % R/H
Test Voltage | 5102 |  | Vdc | Test Voltage | 5103 |  | Vdc | Test Voltage | 5103 |  | Vdc | Test Voltage | 5000 |  | Vdc | Test Voltage | 510 |  | Vdc
Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA)
15 | 1.222 | 0.3055 | 4.1751 | 15 | 1.19 | 0.29957 | 4.2874 | 15 | 1.19 | 0.29957 | 4.2874 | 15 | 0.574 | 0.1445 | 8.8885 | 15 | 0.116 | 0.032854 | 43.9828
30 | 2.45 | 0.6125 | 2.0824 | 30 | 2.2 | 0.55383 | 2.3191 | 30 | 2.2 | 0.55383 | 2.3191 | 30 | 0.934 | 0.23512 | 5.4625 | 30 | 2.54 | 0.71938 | 2.0087
45 | 3.02 | 0.755 | 1.6894 | 45 | 2.92 | 0.73508 | 1.7473 | 45 | 2.92 | 0.73508 | 1.7473 | 45 | 1.288 | 0.32424 | 3.9612 | 45 | 3.29 | 0.9318 | 1.5508
60 | 3.82 | 0.955 | 1.3356 | 60 | 3.57 | 0.89871 | 1.4291 | 60 | 3.57 | 0.89871 | 1.4291 | 60 | 1.589 | 0.40001 | 3.2108 | 60 | 3.92 | 1.1102 | 1.3015
120 | 6.15 | 1.5375 | 0.82959 | 120 | 5.81 | 1.4626 | 0.87814 | 120 | 5.81 | 1.4626 | 0.87814 | 120 | 2.59 | 0.652 | 1.9699 | 120 | 5.96 | 1.688 | 0.85604
180 | 8.08 | 2.02 | 0.63144 | 180 | 7.65 | 1.9258 | 0.66693 | 180 | 7.65 | 1.9258 | 0.66693 | 180 | 3.4 | 0.85591 | 1.5006 | 180 | 7.33 | 2.076 | 0.69604
240 | 9.82 | 2.455 | 0.51955 | 240 | 9.28 | 2.3361 | 0.54978 | 240 | 9.28 | 2.3361 | 0.54978 | 240 | 4.13 | 1.0397 | 1.2354 | 240 | 8.58 | 2.43 | 0.59464
300 | 11.4 | 2.85 | 0.44754 | 300 | 10.81 | 2.7213 | 0.47197 | 300 | 10.81 | 2.7213 | 0.47197 | 300 | 4.93 | 1.2411 | 1.0349 | 300 | 9.61 | 2.7218 | 0.53091
360 | 12.81 | 3.2025 | 0.39828 | 360 | 12.21 | 3.0737 | 0.41785 | 360 | 12.21 | 3.0737 | 0.41785 | 360 | 5.45 | 1.372 | 0.93615 | 360 | 10.83 | 3.0673 | 0.4711
420 | 14.29 | 3.5725 | 0.35703 | 420 | 13.54 | 3.4085 | 0.37681 | 420 | 13.54 | 3.4085 | 0.37681 | 420 | 6.04 | 1.5205 | 0.8447 | 420 | 11.7 | 3.3137 | 0.43607
480 | 15.56 | 3.89 | 0.32789 | 480 | 14.81 | 3.7283 | 0.3445 | 480 | 14.81 | 3.7283 | 0.3445 | 480 | 6.63 | 1.669 | 0.76953 | 480 | 12.43 | 3.5204 | 0.41046
540 | 16.89 | 4.2225 | 0.30207 | 540 | 16.05 | 4.0404 | 0.31788 | 540 | 16.05 | 4.0404 | 0.31788 | 540 | 7.07 | 1.7798 | 0.72164 | 540 | 12.91 | 3.6564 | 0.3952
600 | 18.04 | 4.51 | 0.28282 | 600 | 17.32 | 4.3601 | 0.29457 | 600 | 17.32 | 4.3601 | 0.29457 | 600 | 7.63 | 1.9208 | 0.66868 | 600 | 13.85 | 3.9226 | 0.36838
PI | 4.7225 |  |  | PI | 4.8515 |  |  | PI | 4.8515 |  |  | PI | 4.8018 |  |  | PI | 3.5332
Notes: Min Allowed PI = 1.0 Min Allowed IR1 = 18 Mega-Ohms Data Summary at End of Test: PI = 4.72, 283nA, 168nF, 5103V |  |  |  | Notes: Min Allowed PI = 1.0 Min Allowed IR1 = 18 Mega-Ohms Data Summary at End of Test: PI = 4.85, 295nA, 169nF, 5103V |  |  |  | Notes: File #did not save data Min Allowed PI = 1.0 Min Allowed IR1 = 18 Mega-Ohms Data Summary at End of Test: PI = 4.85, 295nA, 169nF, 5103V |  |  |  | Notes: Min Allowed PI = 1.0 Min Allowed IR1 = 7.1 Mega-Ohms (for 3-phase configuration) Data Summary at End of Test: PI = 4.82, 669nA, 479nF, 5103V |  |  |  | Notes: Min Allowed IR1 = 80 kilo-Ohms Data Summary at End of Test: PI = 3.53, 36.8nA, 81nF, 510V Charging Negative (negative output to winding copper)

## Test #1 (CO2) Fault #1 Data
Generator Stator and Field Winding Insulation Resistance (IR) and Polarization Index (PI) Test Results After Fault #1 with CO2 Fire Suppression Media
Bulk Test (Phase A, B, & C connected together - tested simultaneously) |  |  |  | Field Winding
Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568
Date |  | Start Time |  | Date |  | Start Time
Ambient Temp |  |  | C | Ambient Temp |  |  | C
RTD Temp |  |  | C | Winding IR Temp |  | by IR | C
Humidity |  |  | % R/H | Humidity |  |  | % R/H
Test Voltage |  |  | Vdc | Test Voltage |  |  | Vdc
Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA)
15 |  | 0 | #DIV/0! | 15 |  | 0 | #DIV/0!
30 |  | 0 | #DIV/0! | 30 |  | 0 | #DIV/0!
45 |  | 0 | #DIV/0! | 45 |  | 0 | #DIV/0!
60 |  | 0 | #DIV/0! | 60 |  | 0 | #DIV/0!
120 |  | 0 | #DIV/0! | 120 |  | 0 | #DIV/0!
180 |  | 0 | #DIV/0! | 180 |  | 0 | #DIV/0!
240 |  | 0 | #DIV/0! | 240 |  | 0 | #DIV/0!
300 |  | 0 | #DIV/0! | 300 |  | 0 | #DIV/0!
360 |  | 0 | #DIV/0! | 360 |  | 0 | #DIV/0!
420 |  | 0 | #DIV/0! | 420 |  | 0 | #DIV/0!
480 |  | 0 | #DIV/0! | 480 |  | 0 | #DIV/0!
540 |  | 0 | #DIV/0! | 540 |  | 0 | #DIV/0!
600 |  | 0 | #DIV/0! | 600 |  | 0 | #DIV/0!
PI | #DIV/0! |  |  | PI | #DIV/0!
Notes: File # Min Allowed PI = 1.0 Min Allowed IR1 = 7.1 Mega-Ohms (for 3-phase confirguration) TEST NOT PERFORMED! |  |  |  | Notes: File # Min Allowed IR1 = 80 kilo-Ohms TEST NOT PERFORMED!
Notes: Testing Not performed because fire suppression media did not enter the air housing. In the interest of time this testing was not performed.

## G2 After Fault#2 (HWM) Data
Generator Stator Winding and Field Winding Insulation Resistance (IR) and Polarization Index (PI) Test Results After Fault #2 - Hybrid Fire Suppression System Media
Bulk Test |  |  |  | Field Winding
Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568
Date | 2024-11-20 | Start Time |  | Date | 2024-11-20 | Start Time
Ambient Temp | 20 |  | C | Ambient Temp | 20 |  | C
RTD Temp | 20 |  | C | Winding IR Temp | 20 | by IR | C
Humidity | 25.5 |  | % R/H | Humidity | 25.5 |  | % R/H
Test Voltage | 5101 |  | Vdc | Test Voltage | 509 |  | Vdc
Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA)
15 | 0.513 | 0.12825 | 9.9435 | 15 | 0.87 | 0.2175 | 0.58506
30 | 0.833 | 0.20825 | 6.1236 | 30 | 1.76 | 0.44 | 0.2892
45 | 1.11 | 0.2775 | 4.5955 | 45 | 2.19 | 0.5475 | 0.23242
60 | 1.41 | 0.3525 | 3.6177 | 60 | 2.54 | 0.635 | 0.20039
120 | 2.21 | 0.5525 | 2.3081 | 120 | 3.45 | 0.8625 | 0.14754
180 | 2.86 | 0.715 | 1.7836 | 180 | 4.25 | 1.0625 | 0.11976
240 | 3.48 | 0.87 | 1.4658 | 240 | 4.8 | 1.2 | 0.10604
300 | 4.01 | 1.0025 | 1.2721 | 300 | 5.3 | 1.325 | 0.096038
360 | 4.55 | 1.1375 | 1.1211 | 360 | 5.81 | 1.4525 | 0.087608
420 | 5.01 | 1.2525 | 1.0182 | 420 | 6.2 | 1.55 | 0.082097
480 | 5.51 | 1.3775 | 0.92577 | 480 | 6.48 | 1.62 | 0.078549
540 | 5.92 | 1.48 | 0.86166 | 540 | 6.91 | 1.7275 | 0.073661
600 | 6.37 | 1.5925 | 0.80078 | 600 | 7.24 | 1.81 | 0.070304
PI | 4.5177 |  |  | PI | 2.8504
Notes: Min Allowed PI = 1.0 Min Allowed IR1 = 7.1 Mega-Ohms |  |  |  | Notes: Min Allowed IR1 = 80 kilo-Ohms

## G2 After Fault#3 (HWM) Data
Generator Stator Winding and Field Winding Insulation Resistance (IR) and Polarization Index (PI) Test Results After Fault #3 - Hybrid Fire Suppression System Media
Bulk Test |  |  |  | Field Winding
Test Equipment | Megger S1-1568 |  |  | Test Equipment | Megger S1-1568
Date | 2024-11-20 | Start Time |  | Date | 2024-11-20 | Start Time
Ambient Temp | 20 |  | C | Ambient Temp | 20 |  | C
RTD Temp | 20 |  | C | Winding IR Temp | 20 | by IR | C
Humidity | 25.5 |  | % R/H | Humidity | 25.5 |  | % R/H
Test Voltage | 5101 |  | Vdc | Test Voltage | 509 |  | Vdc
Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA) | Time (s) | Resitance (GΩ) | Corrected to 40C | Current (µA)
15 | 0.45 | 0.1125 | 11.3356 | 15 | 0.835 | 0.20875 | 0.60958
30 | 0.805 | 0.20125 | 6.3366 | 30 | 1.692 | 0.423 | 0.30083
45 | 1.067 | 0.26675 | 4.7807 | 45 | 2.1068 | 0.5267 | 0.2416
60 | 1.39 | 0.3475 | 3.6698 | 60 | 2.48 | 0.62 | 0.20524
120 | 2.12 | 0.53 | 2.4061 | 120 | 3.32 | 0.83 | 0.15331
180 | 2.24 | 0.56 | 2.2772 | 180 | 4.09 | 1.0225 | 0.12445
240 | 3.34 | 0.835 | 1.5272 | 240 | 4.62 | 1.155 | 0.11017
300 | 3.79 | 0.9475 | 1.3459 | 300 | 5.1 | 1.275 | 0.099804
360 | 4.35 | 1.0875 | 1.1726 | 360 | 5.58 | 1.395 | 0.091219
420 | 4.79 | 1.1975 | 1.0649 | 420 | 5.96 | 1.49 | 0.085403
480 | 5.29 | 1.3225 | 0.96427 | 480 | 6.23 | 1.5575 | 0.081701
540 | 5.61 | 1.4025 | 0.90927 | 540 | 6.65 | 1.6625 | 0.076541
600 | 6.09 | 1.5225 | 0.8376 | 600 | 6.96 | 1.74 | 0.073132
PI | 4.3813 |  |  | PI | 2.8065
Notes: Min Allowed PI = 1.0 Min Allowed IR1 = 7.1 Mega-Ohms |  |  |  | Notes: Min Allowed = 80 kilo-Ohms